|  |
| --- |
| Fire Review |
|  |

|  |  |  |
| --- | --- | --- |
| **Collapse** |

|  |
| --- |
| Marked as **Deficiency** on **05/24/2018**  |

 |
|  |

|  |  |  |
| --- | --- | --- |
| **Comment:** |    | Please provide more information. Plan shows doors being replaced. Are any of these doors fire doors. Doors appear to be egress doors from an assembly, Doors may need panic hardware, what type of hardware is there currently and what is being replaced. Also, plan says drywall being replaced, please show on plan where and if any of the walls are rated where being replaced, what rating is and how it will be maintained?? |

 |
|  |
| *Collapse* |

|  |
| --- |
| Marked as **Deficiency** on **06/04/2018**  |

 |  |
|  |

|  |  |  |
| --- | --- | --- |
| **Comment:** |    | 1.Please provide new scalable drawing or call out all dimensions so lengths distances can be measured. 2. Please provide occupant load all areas of this structure?? Is this a stand alone structure or attached to another structure. Is it assembly, business, etc. What will be stored in storage area? 3. Travel distances to exits, are there any rated walls in building. Please provide door schedule with hardware type/ 4. Does the kitchen contain any appliances that produce grease latent vapors that may nee fire AES System? Is the space all one tenant, or will be rented out to Sep. tenants?? Sauna's appear to be installed not submitted in first submittal, what are the manufactures specs, for electric fixtures, heating elements inside sauna's?? Does building have any existing fire alarm or suppression systems? Will new exercise/fitness area require any electric/or maglock type entry system, if so, needs to fail on alarm or power outage. If occupancy is 100 or over, doors need to be equipped with panic hardware, not shown on plan. Doors also, need to swing out towards the means of egress not in.... |

 |  |
|  |

 |